Ref No.:

Date:

To,

Project: ONYX Skyview at Bahrain Bay

Attn:

Subject: 	Technical Submission & Cost Variation Claim – Pressure Rating Upgrade for 13th Floor

Heat Exchangers (PN16 to PN25)

Dear Sir,

Refer MAC No.___________dated: , with a status “Approved with comments”. We are writing to formally submit a technical query and associated cost variation regarding the pressure ratings for the Primary and Secondary Heat Exchangers (HEX) located on the 13th Floor.

1. Background and Tender Basis

During the tender stage, specific pressure ratings for these units were not explicitly defined in the tender requirements. Consequently, we were instructed to mirror the specifications of the "ONYX 1" reference project.

As per the ONYX 1 design, the installed Heat Exchangers were Danfoss units rated at PN16. In strict adherence to the tender instructions to follow the ONYX 1 precedent, our commercial offer and initial technical selection were based on PN16 rated units.

2. Technical Necessity for Pressure Upgrade

Upon detailed design review and calculation of the actual hydraulic parameters for the current project, it has been determined that the operating pressures on the 13th Floor exceed the safe working limits of PN16 equipment (maximum 16 bar).

The detailed pressure calculations are as follows:

A. 13th Floor Primary HEX

Static Head: (Basement 1 to 13th Floor: 21 floors × 3.6m) = 75.6m (7.5 bar)

Pump Maximum Capacity: 5.71 bar

Pressurization Unit Filling Pressure: 5.00 bar

Total Operating Pressure: 18.21 bar

B. 13th Floor Secondary HEX

Static Head: (Serving 25th to 50th Floor) = 133.2m (13.2 bar)

Pump Maximum Capacity: 5.44 bar

Pressurization Unit Filling Pressure: 1.00 bar

Total Operating Pressure: 19.64 bar

3. Conclusion and Variation Claim

As explained above, the Total Operating Pressures of 18.21 bar and 19.64 bar significantly exceed the PN16 rating. To ensure system integrity, safety, and operational reliability, it is technically mandatory to upgrade these Heat Exchangers to PN25 (rated for 25 bar).

As this requirement differs from the tender instruction (to follow the ONYX 1 PN16 specification) and arises from the specific hydraulic heights of this building, we hereby submit this as a variation.

We have attached the detailed cost breakdown for this difference.

Since the lead time is 24-26 weeks from the date of order confirmation, we would appreciate your technical approval of the PN25 selection and subsequent approval of the associated cost variation in order to proceed with procurement as soon as possible.

Attachments:

- Variation price

- Onyx-1 HEX selection

- Onyx skyview HEX selection

- Onyx skyview HEX MAC approved copy